Digital Communication Standard -

Ademco ® Contact ID Protocol -

for Alarm System Communications

SIA DC-05-1999.09

Sponsor

Security Industry Association

Copyright 1999 - Ademco Group

Publication Order Number: 14085

FOREWORD

This standard documents a communications protocol that was developed and is wholly owned by ADEMCO Group, a division of Pittway Corporation.  It is published by the Security Industry Association (SIA) as a de facto security industry standard.  It is intended to facilitate product compatibility and interchangeability, to reduce misunderstandings between manufacturers and purchasers, and to assist purchasers in obtaining the proper products to fulfill their particular needs.

The existence of this or any SIA standards document shall not prevent any SIA member or non-member from manufacturing, selling, or using products not conforming to this or any SIA standard.  SIA standards are voluntary.  SIA encourages the use of this document but will not take any action to ensure compliance with this or any other SIA Standard.

Neither SIA nor Ademco assume any responsibility for the use, application or misapplication of this protocol. Although some SIA standards establish minimum performance requirements, they are intended neither to preclude additional product features or functions nor to act as a maximum performance limit.  Any product, the specifications of which meet the minimum requirements of a SIA standard, shall be considered in compliance with that standard.  Any product, the specifications of which exceed the minimum requirements of a SIA standard, shall also be considered in compliance with the standard, provided that such product specifications do not exceed any maximum requirements set by the standard.  SIA standards are not intended to supersede any recommended procedures set by a manufacturer for its products.

Ademco reserves the right to revise this protocol at any time.  Users of this document are cautioned to obtain and use the most recent edition of this standard.  Current information regarding the revision level or status of this or any other SIA standard may be obtained by contacting SIA.

Requests to modify this document are welcome at any time from any party, regardless of membership affiliation with SIA.  Such requests are to be made in writing, clearly identifying this document and the text within it related to the proposed modification, and include a draft of the proposed changes with supporting comments.  Requests for new Event Codes are to include a description of the event to be reported as well as a short justification.  Submission of requests are to be accompanied by the name, phone number, and e-mail address (if available) of the person making the request.  Requests are to be sent directly to Ademco, preferably by email, care of:

Rich Hinkson: Rich_Hinkson@ademco.com

or

Bob Orlando: Bob_Orlando@ademco.com

Decisions to modify this protocol are at the sole discretion of Ademco, and Ademco reserves the right to deny requests.  When a decision is made regarding a request for modification, Ademco will notify the requestor.  Whenever a modification is made to this protocol, Ademco will inform SIA so that SIA may update this document and notify other interested parties.  Ademco may, at its discretion, also maintain a current list of Event Codes for this protocol on its web site:  http://www.ademco.com

Written requests for interpretations of this standard and other matters of document publication should be addressed to:

Standards
Security Industry Association
635 Slaters Lane,  Suite 110
Alexandria, VA   22314

E-mail: Standards@siaonline.com

Internet:  http://www.siaonline.org

ACKNOWLEDGMENTS

This document was developed by Richard Hinkson of the ADEMCO Group, a division of Pittway Corporation.

The Ademco “Contact ID” protocol has become a prevalent and respected format for digital communications between security alarm systems and central monitoring stations.  Many manufacturers have adopted it, seeking industry wide compatibility.

SIA gratefully acknowledges Ademco’s generous contribution to communications in the security industry, both in allowing SIA to publish this protocol as a de facto security industry standard and in accepting industry requests for modifications.

REVISION HISTORY

The following are changes made to this document, listed by revision.

September 1999 BASELINE

Original Publication

This page intentionally blank.

Table of Contents

1.	SCOPE	1

1.1	Objectives	1

2.	CONVENTIONS AND DEFINITIONS	1

2.1	Conventions	1

2.1.1	Units of Measurement.	1

2.1.2	Tolerances	1

2.1.3	Special Capitalization.	1

2.1.4	Nomenclature and Identification of Sections.	2

2.1.5	Binding Language	2

2.2	Definitions	2

3.	Reference documents	4

4.	Transmission Requirements	4

4.1	Transmission Components	4

4.1.1	Handshake Tones	4

4.1.2	Message Blocks	5

4.1.2.4  Inter-Message Time	6

4.1.3	Kissoff (Acknowledgement) Tone	6

4.1.4	Maximum Number of Attempts	6

Appendix A:   Example Messages	7

Example 1 – Alarm Message	7

Example 2 – Restoral Message	7

Example 3 – Opening Message	8

Appendix B:   Message Transmission Flowchart	9

Appendix C:   Event Codes	10

Digital Communication Standard -

Ademco ® Contact ID Protocol -

for Alarm System Communications

# SCOPE

This standard details the specification for the “Ademco ® Contact ID” communication format, originally developed by the Ademco Group, a division of Pittway Corporation.

The purpose of this standard is to detail the Contact ID signaling format such that it can be adopted by any manufacturer of digital transmitters or receivers.   Documentation and distribution of this communication format is intended to provide an across-the-board compatibility of equipment designed to this standard regardless of manufacturer.

This communications format utilizes standard DTMF tones for transmission of the information.

## Objectives

- Provide information regarding events that are occurring on a customer’s premises. This information should be in a form that can easily be interpreted by a central station operator.

- Spend minimum practical time on line per transaction, to minimize the number of receivers required to handle the traffic and minimize the time the line is seized and not available to the customer.

- Minimize the transmission error rate

- Minimize the cost of the hardware associated with the transmission of the information

# CONVENTIONS AND DEFINITIONS

## Conventions

### Units of Measurement.

In accordance with SIA Policy, the units of measurements used throughout this publication are the units of the System  International d’ Unites (SI), commonly known as metric units.  Equivalent English Units, enclosed in parenthesis, are also used in this publication.  These equivalent English Units are approximate conversions and are provided for easy reference.

### Tolerances

Unless otherwise specified, the tolerance for measurements specified within this standard shall be 10 percent (±10%).

### Special Capitalization.

Alarm sequence events, alarm system commands and states, and digital communication codes transmitted by the control panel to the central station are capitalized within the text of this standard.

### Nomenclature and Identification of Sections.

Sections within this standard are identified and referenced by the number preceding each section.  Unless otherwise specified, references to a section refer to only that section and not to subsequent subsections within the section.

### Binding Language

This standard uses the term “shall” to convey binding requirements.

The term “may” is used to convey features that are allowed but not required.

Terms such as “is”, “are”, “will”, and others are used to convey statements of fact for advisory purposes only.

The annotation “Note:” also precedes advisory information

## Definitions

For the purpose of this standard, the following terms have the meaning indicated.

Abort - A manual intervention during a process that prevents completion of that process.

Access Code, or Code - A series of digits that a user enters on a keypad to access the system for arming or disarming.

Account, or Account Number - Information that identifies a particular alarm panel.

ACK, see Acknowledgment.

Acknowledgment, or ACK, or Positive Acknowledgment - A signal sent from one participant in the communication process to the other indicating that the data has been correctly received.

Alarm - An indication of an emergency condition.  The condition may be that of an intrusion, a fire, a medical panic, etc.  Locally the condition usually causes visual and/or audible annunciation.  In a system that is monitored, this condition is transmitted to remote equipment.

Alarm Panel - see Control.

Alarm Cancel, or Manual Reset - An action restoring the alarm panel to a non-alarm state.  Also the transmission of that change indicating that the previous alarm signal is to be disregarded.

Alarm Verification – Generic name given to many techniques used to confirm or deny the validity of alarms signals received at the monitoring facility.  (Also see Verified Alarm)

Arm - To turn on a security system.

Area - A defined section of the protected system that can be armed and disarmed independently.  This is sometimes also referred to as a partition.  When areas are used, they are numbered consecutively beginning with 1.

Bypass - To cause a system to ignore input changes from a given point or zone, regardless of the arming state.  Bypassed points and zones do not cause alarm events.  (Also see Zone Bypass, Unbypass)

Close, or Closing - The manual or automatic arming of a security system.  (Also see Early to Close, Fail to Close, Late to Close)

Code -  see Access Code, User Code

Control, Control Panel, or Alarm Panel - The part of a security system that handles control and communication, whether as combined or separate physical units.

Disarm - To turn off a security system (except for 24 hr devices).

DTMF or Dual Tone Multi-Frequency – A standard signaling method for dialing and data transmission using a combination of two sine waves at different frequencies. It is commonly referred to as Touch-Tone® signaling.

Duress - A code that can be entered if one or more persons try to force an individual to enter, or re-enter, a facility against the individual’s will.

Early to Close, or ETC - An event created by the arming of a system before a specified time.

Early to Open, or ETO - An event created by the disarming of a system before a specified time.

Entry Delay or Entry Time - The period of time allowed, after entry to the premises, to disarm the security system before tripping an alarm.

Exit Error – A signal produced by a point or zone that is still violated when the exit time has expired.

Exit Delay, or Exit Time - The period of time allowed, after arming a security system, to exit the premises before tripping an alarm.

Fail to Close, or FTC - An event created by the system at a preset time if it remains in the disarmed state.

Fail to Open, or FTO - An event created by the system at a preset time if it remains in the armed state.

Handshake - A signal sent by one end of the communication channel to the other indicating reception of signal.

Keypad - The part(s) of a security system from which a human operator can arm and disarm the system, manipulate the system operation, or otherwise interact with the system.

Late to Close, or LTC - An event created by the arming of a system after a specified time.

Late to Open, or LTO - An event created by the disarming of a system after a specified time.

Open, or Opening - The manual or automatic disarming of a security system  (see also Early to Open, Fail to Open, Late to Open)

Panic - A general type of perceived emergency, including the presence of one or more unwanted persons trying to gain entry or observed intruders on the private grounds.

Partition - see Area.

Point – an electronically addressable sensor, sometimes used interchangeably with the term sensor. The term is usually used in multiplex alarm systems or for RF (wireless) sensors.

Receiver - The equipment located at the central station that communicates with a control panel.

Recent Closing - A transmission indicating that the security system has recently been armed.

Report - An electronic transmission sent by the control panel to the central station containing detailed information about an event detected by or a status of the security system.

Sounder - An audible annunciator producing sufficient volume to be heard by person(s) within the protected premises.

Subscriber - see User.

Supervisory Signal - A signal indicating the need of action in connection with the supervision of guard tours, fire suppression systems or equipment, or with the maintenance features of related systems. (Not to be confused with a Trouble signal generated from a supervised zone or point.)

Transmitter - The part of the security system that sends electronic data outside the system, typically to a central station.  (Also see Control Panel.)

Trip - An alarm state produced as a result of detection by a sensor.

Trouble – A signal sent to indicate a malfunction, miss-operation, or loss of contact with a supervised zone or point.

Unbypass - To restore a point or zone to normal functioning by removing a bypass condition.

User - The person(s) at the alarm panel site that operate and/or have access to the system.

User Code - see Access Code.

Verified Alarm – An alarm that has been confirmed by monitoring facility contact with the protected premises or an authorized user agent, an alarm from sequentially detected and reported events, a multiple-sensor detected event, or an alarm reported by a system user.  (Also see Alarm Verification.)

Zone - A dedicated input to the control panel containing one or more sensor devices that will trip the input upon activation of any one-sensor device.

Zone Bypass - see Bypass

# Reference documents

This de facto standard does not rely on any other documents for implementation.

Information regarding a specific product that has implemented this de facto standard should be obtained from the manufacturer of that product.

Other unrelated standards for digital communications may be obtained from the Security Industry Association.

# Transmission Requirements

This section describes the basic components of a communication session.

## Transmission Components

The transmitter to receiver communication session is composed of three basic elements: the Handshake Tone sequence, Message Blocks, and Acknowledgements.

The Handshake Tone sequence consists of a pair of single-frequency tones sequenced in time.

The Message Blocks consist of a series of DTMF tone bursts separated by spaces.

The Acknowledgement Tone is a single tone burst.

### Handshake Tones

The Handshake Tone sequence is produced by the RECEIVER. The purpose is to signal the TRANSMITTER that the communication channel is ready.

#### Placement

The Handshake Tone sequence is emitted by the receiver after going off-hook and delaying an interval of at least 0.5 seconds but typically no greater than 2.0 seconds. This time allows the phone network connection to settle before the communication process begins.

#### Composition

The handshake tone sequence shall consist of:

- A burst of 1400 Hz. ±3% tone with a duration of 100 msec. ±5%

- A pause of 100 msec. ±5%

- A burst of 2300 Hz. ±3% tone with a duration of 100 msec. ±5%

Note:  Transmitters shall accept a frequency error of at least ± 5% to ensure back-compatibility with older receivers.

### Message Blocks

A Message Block is sent by the TRANSMITTER for each message in the transmitter’s message queue. Each message block contains sufficient information to report an event in the system.

#### Placement

The first message block is sent beginning 250 msec. (250 min.,300 max.) after the end of either the Handshake Tone sequence or after a Kissoff (Acknowledgement) tone. The delay is timed from the end of the tone.

#### Message Composition

The form of the message is:

ACCT MT QXYZ GG CCC

where:

ACCT = 4 Digit Account number (0-9, B-F)

MT = Message Type. This 2-digit sequence is used to identify the Contact ID message to the receiver. It may be transmitted as either 18 (preferred) or 98 (optional). New receiver implementations shall accept either a 18 or a 98. Note that some older receivers may not accept 98 .

Q = Event qualifier, which gives specific event information:

1 = New Event or Opening

3 = New Restore or Closing

6 = Previously reported condition still present (Status report)

XYZ = Event code (3 Hex digits 0-9,B-F)

GG = Group or Partition number (2 Hex digits 0-9, B-F).  Use 00 to indicate that no specific group or partition information applies.

CCC = Zone number (Event reports) or User # (Open / Close reports ) (3 Hex digits 0-9,B-F ).  Use 000 to indicate that no specific zone or user information applies

S = 1 Digit Hex checksum calculated such that:

(Sum of all message digits + S) MOD 15 = 0

Note:  A ‘0’ shall be transmitted as a 10 and valued as a 10 for checksum purposes even though it is displayed and printed as ‘0’. It uses the same tone pair as the ‘0’ (OPER) key on a standard telephone.

#### Data Tones

The message is sent using standard DTMF tones.

The timing of the tones shall be as follows:

Burst ON time - 50 msec. (50 min.,60 max.)

Burst OFF time- 50 msec. (50 min.,60 max.)

The details of the tones are contained in the following table.

Data Transmission Frequencies -

Standard DTMF Signaling

| Digit | Low Tone (Hz.) | High Tone (Hz. ) | Digit Value |
| --- | --- | --- | --- |
| 0 | 941 | 1336 | 10 |
| 1 | 697 | 1209 | 1 |
| 2 | 697 | 1336 | 2 |
| 3 | 697 | 1477 | 3 |
| 4 | 770 | 1209 | 4 |
| 5 | 770 | 1336 | 5 |
| 6 | 770 | 1477 | 6 |
| 7 | 852 | 1209 | 7 |
| 8 | 852 | 1336 | 8 |
| 9 | 852 | 1477 | 9 |
| B (*) | 941 | 1209 | 11 |
| C (#) | 941 | 1477 | 12 |
| D | 697 | 1633 | 13 |
| E | 770 | 1633 | 14 |
| F | 852 | 1633 | 15 |

Notes:

- The digit ‘0’ is transmitted with a value of 10 and shall be counted as a 10 in the calculation of the message checksum.

- The DTMF pair of 941 Hz. And 1633 Hz. is not used in this format and shall not be sent.

- The frequency deviation on each of the above frequencies shall be ± 1.5% max.

### 4.1.2.4  Inter-Message Time

After sending its message, the transmitter should wait for 1.25 sec. for the start of a Kissoff Tone from the receiver. If the start of a kissoff tone is detected, the transmitter must continue timing the tone, even if the inter-message time expires. The panel must detect a minimum of 400 msec. of the Kissoff Tone for it to be considered to be valid.

If a Kissoff tone is detected, the transmitter should wait for the tone to end and then wait 250 msec. (250 min.,300 max.) before beginning the next message.

If no Kissoff Tone is received, the transmitter should repeat the message after the expiration of the 1.25 second inter-message interval.

### Kissoff (Acknowledgement) Tone

The Kissoff tone from the receiver is used to tell the transmitter that the message has been received successfully. The frequency of the tone shall be 1400 Hz. ±3% and shall be sent by the receiver for a minimum of 750 msec. and a maximum period of 1 second.

The transmitter must detect a minimum of 400 msec. of tone before considering the kissoff to be valid.

Note: Transmitters shall accept a frequency error of at least ± 5% to ensure back-compatibility with older receivers

### Maximum Number of Attempts

The transmitter shall make up to 4 attempts to deliver a message before hanging up and redialing. The attempts counter is reset each time a valid kissoff signal is received.

## Data Codes

The data codes used to transmit events are contained in Appendix C: Event Codes.

# Appendix A:   Example Messages

## Example 1 – Alarm Message

Account 1234 is reporting a Perimeter Burglary Alarm on Zone 15 of Partition 1

The message shall be sent as:

1234 18 1131 01 015 8

where:

1234	=	The account number  (1234)

18	=	The message type used to identify the message as Contact ID

1131	=	The Event Qualifier (1) for a new event, followed by the Event Code for Perimeter Burglary (131)

01	=	The partition number (1)

015	=	The zone number (015)

8	=	The checksum, computed in the following manner:

- Add all of the message digits together, using 10 for all ‘0’ digits (1+2+3+4)+(1+8)+(1+1+3+1)+(10+1)+(10+1+5) = 52

- Find the next highest multiple of 15, in this case 60.

- Subtract the sum from this value (60-52 = 8)

- Use the result for the checksum.. If the result is 0, use the digit ‘F’ (15) for the checksum.

## Example 2 – Restoral Message

Account 1234 is reporting a Restore of a Perimeter Burglary Alarm on Zone 15 of Partition 1

The message shall be sent as:

1234 18 3131 01 015 6

where:

1234 	=	The account number  (1234)

18 	=	The message type used to identify the message as Contact ID

3131    =	The Event Qualifier (3) for a restoral, followed by the Event Code for Perimeter Burglary (131)

01	=	The partition number (1)

015	=	The zone number (015)

6	=	The checksum (See Example 1)

## Example 3 – Opening Message

User 3 disarms Partition 2 of Account 1234

The message shall be sent as:

1234 18 1401 02 003 5

where

1234 	=	The account number  (1234)

18 	=	The message type used to identify the message as Contact ID

1401   =	The Event Qualifier (1) for an Opening, followed by the Event Code for Open/Close by User (401)

02	=	The partition number (2)

003	=	The User number (003)

5	=	The checksum (See Example 1)

Example 4 – Closing Message

User 5 arms Partition 3 of Account 1234

The message shall be sent as:

1234 18 3401 03 005 F

where

1234	=	The account number  (1234)

18	=	The message type used to identify the message as Contact ID

3401	=	The Event Qualifier (3) for a Closing, followed by the Event Code for Open/Close by User (401)

03	=	The partition number (2)

005	=	The User number (003)

F	=	The checksum (See Example 1)

Note the use of ‘F’ since the sum of the message digits is an even multiple of 15.

# Appendix B:   Message Transmission Flowchart

# Appendix C:   Event Codes

100

ALARMS

200

SUPERVISORY

300

TROUBLES

400

OPEN/CLOSE

REMOTE ACCESS

500

BYPASSES/DISABLES

600

TEST/ MISC

EVENT CODE CLASSIFICATIONS

MedicalFireSystemOpen/CloseSystemTestFireSounder/RelayRemote AccessSounder/RlyLogPanicSys. Per.Access ControlSys. Per.Sched.BurglaryComm.Comm.GeneralProt. Loop24 HourSensor

Notes on Event Code definitions

- The following table defines the Event Codes used in this protocol.

- The Data Type identifies the information sent in the CCC field as either Zone number or User number.

- The value in the CCC field should be set to 000 if no useful information is being sent.

- Descriptions for the Event Codes will be added in a later revision of this standard.

| Event | Data Type | Descriptions (to be supplied in a later revision of this standard) |
| --- | --- | --- |
| ALARMS |  |  |
| Medical Alarms –100 |  |  |
| 100 Medical | Zone |  |
| 101 Personal Emergency | Zone |  |
| 102 Fail to report in | Zone |  |
| Fire Alarms –110 |  |  |
| 110 Fire | Zone |  |
| 111 Smoke | Zone |  |
| 112 Combustion | Zone |  |
| 113 Water flow | Zone |  |
| 114 Heat | Zone |  |
| 115 Pull Station | Zone |  |
| 116 Duct | Zone |  |
| 117 Flame | Zone |  |
| 118 Near Alarm | Zone |  |
| Panic Alarms –120 |  |  |
| 120 Panic | Zone |  |
| 121 Duress | User |  |
| 122 Silent | Zone |  |
| 123 Audible | Zone |  |
| 124 Duress – Access granted | Zone |  |
| 125 Duress – Egress granted | Zone |  |
| Burglar Alarms –130 |  |  |
| 130 Burglary | Zone |  |
| 131 Perimeter | Zone |  |
| 132 Interior | Zone |  |
| 133 24 Hour (Safe) | Zone |  |
| 134 Entry/Exit | Zone |  |
| 135 Day/night | Zone |  |
| 136 Outdoor | Zone |  |
| 137 Tamper | Zone |  |
| 138 Near alarm | Zone |  |
| 139 Intrusion Verifier | Zone |  |
| General Alarm – 140 |  |  |
|  | Zone |  |
| 140 General Alarm | Zone |  |
| 141 Polling loop open | Zone |  |
| 142 Polling loop short | Zone |  |
| 143 Expansion module failure | Zone |  |
| 144 Sensor tamper | Zone |  |
| 145 Expansion module tamper | Zone |  |
| 146 Silent Burglary | Zone |  |
| 147 Sensor Supervision Failure | Zone |  |
| 24 Hour Non-Burglary - 150 and 160 |  |  |
| 150 24 Hour Non-Burglary | Zone |  |
| 151 Gas detected | Zone |  |
| 152 Refrigeration | Zone |  |
| 153 Loss of heat | Zone |  |
| 154 Water Leakage | Zone |  |
| 155 Foil Break | Zone |  |
| 156 Day Trouble | Zone |  |
| 157 Low bottled gas level | Zone |  |
| 158 High temp | Zone |  |
| 159 Low temp | Zone |  |
| 161 Loss of air flow | Zone |  |
| 162 Carbon Monoxide detected | Zone |  |
| 163 Tank level | Zone |  |
| SUPERVISORY |  |  |
| Fire Supervisory - 200 and 210 |  |  |
| 200 Fire Supervisory | Zone |  |
| 201 Low water pressure | Zone |  |
| 202 Low CO2 | Zone |  |
| 203 Gate valve sensor | Zone |  |
| 204 Low water level | Zone |  |
| 205 Pump activated | Zone |  |
| 206 Pump failure | Zone |  |
| TROUBLES |  |  |
| System Troubles -300 and 310 |  |  |
| 300 System Trouble | Zone |  |
| 301 AC Loss | Zone |  |
| 302 Low system battery | Zone |  |
| 303 RAM Checksum bad | Zone |  |
| 304 ROM checksum bad | Zone |  |
| 305 System reset | Zone |  |
| 306 Panel programming changed | Zone |  |
| 307 Self-test failure | Zone |  |
| 308 System shutdown | Zone |  |
| 309 Battery test failure | Zone |  |
| 310 Ground fault | Zone |  |
| 311 Battery Missing/Dead | Zone |  |
| - Power Supply Overcurrent | Zone |  |
| 313 Engineer Reset | User |  |
| Sounder / Relay Troubles -320 |  |  |
| 320 Sounder/Relay | Zone |  |
| 321 Bell 1 | Zone |  |
| 322 Bell 2 | Zone |  |
| 323 Alarm relay | Zone |  |
| 324 Trouble relay | Zone |  |
| 325 Reversing relay | Zone |  |
| 326 Notification Appliance Ckt. # 3 | Zone |  |
| 327 Notification Appliance Ckt. #4 | Zone |  |
| System Peripheral Trouble -330 and 340 |  |  |
| 330 System Peripheral trouble | Zone |  |
| 331 Polling loop open | Zone |  |
| 332 Polling loop short | Zone |  |
| 333 Expansion module failure | Zone |  |
| 334 Repeater failure | Zone |  |
| 335 Local printer out of paper | Zone |  |
| 336 Local printer failure | Zone |  |
| 337 Exp. Module DC Loss | Zone |  |
| 338 Exp. Module Low Batt. | Zone |  |
| 339 Exp. Module Reset | Zone |  |
| 341 Exp. Module Tamper | Zone |  |
| 342 Exp. Module AC Loss | Zone |  |
| 343 Exp. Module self-test fail | Zone |  |
| 344 RF Receiver Jam Detect | Zone |  |
| Communication Troubles -350 and 360 |  |  |
| 350 Communication trouble | Zone |  |
| 351 Telco 1 fault | Zone |  |
| 352 Telco 2 fault | Zone |  |
| 353 Long Range Radio xmitter fault | Zone |  |
| 354 Failure to communicate event | Zone |  |
| 355 Loss of Radio supervision | Zone |  |
| 356 Loss of central polling | Zone |  |
| 357 Long Range Radio VSWR problem | Zone |  |
| Protection Loop -370 |  |  |
| 370 Protection loop | Zone |  |
| 371 Protection loop open | Zone |  |
| 372 Protection loop short | Zone |  |
| 373 Fire trouble | Zone |  |
| 374 Exit error alarm (zone) | Zone |  |
| 375 Panic zone trouble | Zone |  |
| 376 Hold-up zone trouble | Zone |  |
| 377 Swinger Trouble | Zone |  |
| 378 Cross-zone Trouble | Zone |  |
| Sensor Trouble -380 |  |  |
| 380 Sensor trouble | Zone |  |
| 381 Loss of supervision - RF | Zone |  |
| 382 Loss of supervision - RPM | Zone |  |
| 383 Sensor tamper | Zone |  |
| 384 RF low battery | Zone |  |
| 385 Smoke detector Hi sensitivity | Zone |  |
| 386 Smoke detector Low sensitivity | Zone |  |
| 387 Intrusion detector Hi sensitivity | Zone |  |
| 388 Intrusion detector Low sensitivity | Zone |  |
| 389 Sensor self-test failure | Zone |  |
| 391 Sensor Watch trouble | Zone |  |
| 392 Drift Compensation Error | Zone |  |
| 393 Maintenance Alert | Zone |  |
| OPEN/CLOSE/REMOTE ACCESS |  |  |
| Open/Close -400, 440,450 |  |  |
| 400 Open/Close | User |  |
| 401 O/C by user | User |  |
| 402 Group O/C | User |  |
| 403 Automatic O/C | User |  |
| 404 Late to O/C (Note: use 453, 454 instead ) | User |  |
| 405 Deferred O/C (Obsolete- do not use ) | User |  |
| 406 Cancel | User |  |
| 407 Remote arm/disarm | User |  |
| 408 Quick arm | User |  |
| 409 Keyswitch O/C | User |  |
| 441 Armed STAY | User |  |
| 442 Keyswitch Armed STAY | User |  |
| 450 Exception O/C | User |  |
| 451 Early O/C | User |  |
| 452 Late O/C | User |  |
| 453 Failed to Open | User |  |
| 454 Failed to Close | User |  |
| 455 Auto-arm Failed | User |  |
| 456 Partial Arm | User |  |
| 457 Exit Error (user) | User |  |
| 458 User on Premises | User |  |
| 459 Recent Close | User |  |
| 461 Wrong Code Entry | Zone |  |
| 462 Legal Code Entry | User |  |
| 463 Re-arm after Alarm | User |  |
| 464 Auto-arm Time Extended | User |  |
| 465 Panic Alarm Reset | Zone |  |
| 466 Service On/Off Premises | User |  |
| Remote Access –410 |  |  |
| 411 Callback request made | User |  |
| 412 Successful download/access | User |  |
| 413 Unsuccessful access | User |  |
| 414 System shutdown command received | User |  |
| 415 Dialer shutdown command received | User |  |
| 416 Successful Upload | Zone |  |
| Access control –420,430 |  |  |
| 421 Access denied | User |  |
| 422 Access report by user | User |  |
| 423 Forced Access | Zone |  |
| 424 Egress Denied | User |  |
| 425 Egress Granted | User |  |
| 426 Access Door propped open | Zone |  |
| 427 Access point Door Status Monitor trouble | Zone |  |
| 428 Access point Request To Exit trouble | Zone |  |
| 429 Access program mode entry | User |  |
| 430 Access program mode exit | User |  |
| 431 Access threat level change | User |  |
| 432 Access relay/trigger fail | Zone |  |
| 433 Access RTE shunt | Zone |  |
| 434 Access DSM shunt | Zone |  |
| BYPASSES / DISABLES |  |  |
| System Disables -500 and 510 |  |  |
| 501 Access reader disable | Zone |  |
| Sounder / Relay Disables -520 |  |  |
| 520 Sounder/Relay Disable | Zone |  |
| 521 Bell 1 disable | Zone |  |
| 522 Bell 2 disable | Zone |  |
| 523 Alarm relay disable | Zone |  |
| 524 Trouble relay disable | Zone |  |
| 525 Reversing relay disable | Zone |  |
| 526 Notification Appliance Ckt. # 3 disable | Zone |  |
| 527 Notification Appliance Ckt. # 4 disable | Zone |  |
| System Peripheral Disables -530 and 540 |  |  |
| 531 Module Added | Zone |  |
| 532 Module Removed | Zone |  |
| Communication Disables -550 and 560 |  |  |
| 551 Dialer disabled | Zone |  |
| 552 Radio transmitter disabled | Zone |  |
| 553 Remote Upload/Download disabled | Zone |  |
| Bypasses –570 |  |  |
| 570 Zone/Sensor bypass | Zone |  |
| 571 Fire bypass | Zone |  |
| 572 24 Hour zone bypass | Zone |  |
| 573 Burg. Bypass | Zone |  |
| 574 Group bypass | User |  |
| 575 Swinger bypass | Zone |  |
| 576 Access zone shunt | Zone |  |
| 577 Access point bypass | Zone |  |
| TEST / MISC. |  |  |
| Test/Misc. –600, 610 |  |  |
| 601 Manual trigger test report | Zone |  |
| 602 Periodic test report | Zone |  |
| 603 Periodic RF transmission | Zone |  |
| 604 Fire test | User |  |
| 605 Status report to follow | Zone |  |
| 606 Listen-in to follow | Zone |  |
| 607 Walk test mode | User |  |
| 608 Periodic test - System Trouble Present | Zone |  |
| 609 Video Xmitter active | Zone |  |
| 611 Point tested OK | Zone |  |
| 612 Point not tested | Zone |  |
| 613 Intrusion Zone Walk Tested | Zone |  |
| 614 Fire Zone Walk Tested | Zone |  |
| 615 Panic Zone Walk Tested | Zone |  |
| 616 Service Request | Zone |  |
| Event Log –620 |  |  |
| 621 Event Log reset | Zone |  |
| 622 Event Log 50% full | Zone |  |
| 623 Event Log 90% full | Zone |  |
| 624 Event Log overflow | Zone |  |
| 625 Time/Date reset | User |  |
| 626 Time/Date inaccurate | Zone |  |
| 627 Program mode entry | Zone |  |
| 628 Program mode exit | Zone |  |
| 629 32 Hour Event log marker | Zone |  |
| Scheduling –630 |  |  |
| 630 Schedule change | Zone |  |
| 631 Exception schedule change | Zone |  |
| 632 Access schedule change | Zone |  |
| Personnel Monitoring -640 |  |  |
| 641 Senior Watch Trouble | Zone |  |
| 642 Latch-key Supervision | User |  |
| Misc. -650 |  |  |
| 651 Reserved for Ademco Use | Zone |  |
| 652 Reserved for Ademco Use | User |  |
| 653 Reserved for Ademco Use | User |  |
| 654 System Inactivity | Zone |  |

Security Industry Association

635 Slaters Lane,  Suite 110

Alexandria, VA   22314

Standards@SIAOnline.org